## Sheet1
TO LOCK THE KEYBOARD
1. Keep pressed for more than 3s the UP and DOWN keys.
HOW TO CHANGE A PARAMETER VALUE
HOW TO ENTER THE HIDDEN MENU 1. Enter the Programming mode by pressing the SET+DOWN keys for 3s (“°F” LED starts blinking). 2. Released the keys, then push again the SET+DOWN keys for more than 7s. The L2 label will be displayed immediately followed from the Hy parameter. NOW YOU ARE IN THE HIDDEN MENU. 3. Select the required parameter. 4. Press the “SET” key to display its value 5. Use UP or DOWN to change its value. 6. Press “SET” to store the new value and move to the following parameter. To exit: Press SET+UP or wait 15s without pressing a key.

## Refrigerator
Code | Decription | From Factory
Hy | Differential: (0,1°C  25°C / 1°F ÷ 45°F) Intervention differential for set point. Compressor Cut IN is SET POINT + differential (Hy). Compressor Cut OUT is when the temperature reaches the set point. | 6℉
LS | Minimum SET POINT: (-55°C÷SET/-67°F÷SET): Sets the minimum value for the set point.. | 32℉
US | Maximum SET POINT: (SET÷99°C/ SET÷99°F). Set the maximum value for set point. | 41℉
ot | First probe calibration: (-9.9÷9.9°C / -17°F ÷ 17°F) allows to adjust possible offset of the first probe. | 0
P2 | Evaporator probe presence: n= not present; y= the defrost stops by temperature. | n
oE | Second probe calibration: (-9.9÷9.9°C / -17°F ÷ 17°F) allows to adjust possible offset of the second probe. | 0
od | Outputs activation delay at start up: (0÷99min) This function is enabled at the initial start-up of the instrument and inhibits any output activation for the period of time set in the parameter. | 2
AC | Anti-short cycle delay: (0÷50 min) minimum interval between the compressor stop and the following restart. | 5
Cy | Compressor ON time with faulty probe: (0÷99 min) time during which the compressor is active in case of faulty thermostat probe. With Cy=0 compressor is always OFF. | 15
Cn | Compressor OFF time with faulty probe: (0÷99 min) time during which the compressor is OFF in case of faulty thermostat probe. With Cn=0 compressor is always active. | 30
CF | Measurement unit: (°C÷°F) °C =Celsius; °F =Fahrenheit. WARNING: When the measurement unit is changed the SET point and the values of the parameters Hy, LS, US, oE, o1, AU, AL have to be checked and modified if necessary. | ℉
rE | Resolution (only for °C):(dE ÷ in) dE= decimal between -9.9 and 9.9°C; in= integer | in
Ld |  | P1
dy | Display delay: (015 min.) when the temperature increases, the display is updated of 1 °C/1°F after this time. | 1
dE | Defrost termination temperature: (-55÷50°C / -67÷99°F) if P2=Y it sets the temperature measured by the evaporator probe, which causes the end of defrost. | 55℉
do | Set for fan regulation: (-55÷50°C / -67÷99°F); See parameters F1 and F2 | 29
id | Interval between defrost cycles: (0÷99 minutes) Determines the time interval between the beginning of two defrost cycles. | 6
Nd | Maximum length for defrost: (0÷99 min. with 0 no defrost) when P2=n, (not evaporator probe: timed defrost) it sets the defrost duration, when P2 = y (defrost end based on temperature) it sets the maximum length for defrost. | 30
dd | Start defrost delay: ( 0÷99min) This is useful when different defrost start times are necessary to avoid overloading the plant | 1
dF | Display during defrost: (rt / it / SP / dF) rt= real temperature; it= start defrost temperature; SP=SET-POINT; dF= label dF. | it
F1 | Fans operating mode with SET >= do: (cn, on, cY, oY) cn= in runs with the compressor, OFF during defrost; on= continuous mode, OFF uring defrost;; cY= runs with the compressor, ON during defrost; oY= continuous mode, ON during defrost. | oy | oy | when you are on site, Please change F1 to oy and F2 to on
F2 | Fans operating mode with SET < do: (cn, on, cY, oY) cn= in runs with the compressor, OFF during defrost; on= continuous mode, OFF during defrost;; cY= runs with the compressor, ON during defrost; oY= continuous mode, ON during defrost. | on | on
Fd | Fans delay after defrost: (0÷99 min) Interval between end of defrost and evaporator fans start. | 2
FS | Fans stop temperature: (-55÷50°C / -67°F ÷ 99°F) setting of temperature, detected by evaporator probe, above which fans are always OFF. | 99℉
Fn | Fan ON time: (0÷15 min) with F1 or F2 = Cn or Cy, (fan activated in parallel with compressor). it sets the evaporator fan ON cycling time when the compressor is off. With Fn =0 and FF ≠ 0 the fan are always off, with Fn=0 and FF =0 the fan are always off. | 1
FF | Fan OFF time: (0÷15 min) with F1 or F2 = Cn or Cy, (fan activated in parallel with compressor). it sets the evaporator fan off cycling time when the compressor is off. With Fn =0 and FF ≠ 0 the fan are always off, with Fn=0 and FF =0 the fan are always off. | 3
AL | Minimum temperature alarm: (-55÷AU°C /-67÷AU°F) when this temperature is reached the alarm is enabled, after the “Ad” delay time. | -67℉
AU | Maximum temperature alarm: (AL÷99°C/99°F) when this emperature is reached the alarm is enabled, after the “Ad” delay time. | 99℉
Ad | Temperature alarm delay: (0÷99 min) time interval between the detection of an alarm condition and alarm signalling. | 60
dA | Exclusion of temperature alarm at startup: (0÷99 min) time interval between the detection of the temperature alarm condition after instrument power on and alarm signalling. | 90
iP | Digital input polarity: (oP ÷ cL) oP= activated by closing the contact; cL= activated by opening the contact; | cL
iF | Digital input configuration: (EA/bA/do/dF/Au/Hc) EL= external alarm: “EA” message is displayed; bA= serious alarm “CA” message is displayed; PA = do not set it; do= door switch function; dF= defrost activation; Au =not used; Hc= inversion of the kind of action; Fn, ES = do not set it | EL
di | Digital input delay: (0÷99 min) with iF=EA or bA delay between the detection of the external alarm condition and its signalling. . With iF=do it represents the delay to activate the door open alarm. | 5
dC | Compressor and fan status when open door: (no/Fn/cP/Fc): no= normal; Fn = Fans OFF; cP =Compressor OFF; Fc = Compressor and fans OFF; | Fn
rd | Regulation with door open: (n÷y) n = no regulation if door is pened; Y= when di is elapsed regulation restarts even if door open alarm is present; | y

## Freezer
Code | Decription | From Factory
Hy | Differential: (0,1°C  25°C / 1°F ÷ 45°F) Intervention differential for set point. Compressor Cut IN is SET POINT + differential (Hy). Compressor Cut OUT is when the temperature reaches the set point. | 6℉
LS | Minimum SET POINT: (-55°C÷SET/-67°F÷SET): Sets the minimum value for the set point.. | -10℉
US | Maximum SET POINT: (SET÷99°C/ SET÷99°F). Set the maximum value for set point. | 5℉
ot | First probe calibration: (-9.9÷9.9°C / -17°F ÷ 17°F) allows to adjust possible offset of the first probe. | 0
P2 | Evaporator probe presence: n= not present; y= the defrost stops by temperature. | y
oE | Second probe calibration: (-9.9÷9.9°C / -17°F ÷ 17°F) allows to adjust possible offset of the second probe. | 0
od | Outputs activation delay at start up: (0÷99min) This function is enabled at the initial start-up of the instrument and inhibits any output activation for the period of time set in the parameter. | 3
AC | Anti-short cycle delay: (0÷50 min) minimum interval between the compressor stop and the following restart. | 5
Cy | Compressor ON time with faulty probe: (0÷99 min) time during which the compressor is active in case of faulty thermostat probe. With Cy=0 compressor is always OFF. | 15
Cn | Compressor OFF time with faulty probe: (0÷99 min) time during which the compressor is OFF in case of faulty thermostat probe. With Cn=0 compressor is always active. | 15
CF | Measurement unit: (°C÷°F) °C =Celsius; °F =Fahrenheit. WARNING: When the measurement unit is changed the SET point and the values of the parameters Hy, LS, US, oE, o1, AU, AL have to be checked and modified if necessary. | ℉
rE | Resolution (only for °C):(dE ÷ in) dE= decimal between -9.9 and 9.9°C; in= integer | in
Ld |  | P1
dy | Display delay: (015 min.) when the temperature increases, the display is updated of 1 °C/1°F after this time. | 1
td | Defrost type: (EL, in, Ar) EL= electrical heater, compressor OFF; in= hot gas, compressor ON; Ar: defrost according to the value of SET and “do” parameters following conditions: SET > = do: compr. relay off, defrost relay off, fan according to F1 SET < do: compr. relay off, defrost relay on, fan according to F2 | Ar-None GR in-GR unit
dE | Defrost termination temperature: (-55÷50°C / -67÷99°F) if P2=Y it sets the temperature measured by the evaporator probe, which causes the end of defrost. | 55℉
do | Set for fan regulation: (-55÷50°C / -67÷99°F); See parameters F1 and F2 | 29
id | Interval between defrost cycles: (0÷99 minutes) Determines the time interval between the beginning of two defrost cycles. | 6
Nd | Maximum length for defrost: (0÷99 min. with 0 no defrost) when P2=n, (not evaporator probe: timed defrost) it sets the defrost duration, when P2 = y (defrost end based on temperature) it sets the maximum length for defrost. | 30
dd | Start defrost delay: ( 0÷99min) This is useful when different defrost start times are necessary to avoid overloading the plant | 1
dF | Display during defrost: (rt / it / SP / dF) rt= real temperature; it= start defrost temperature; SP=SET-POINT; dF= label dF. | it
dt | Drip time: (0÷99 min) time interval between reaching defrost rmination temperature and the restoring of the control’s normal operation. This time allows the evaporator to eliminate water drops that might have formed due to defrost. | 2
dP | Defrost at power –on: (y÷n) y= at power on defrost starts; n= defrost doesn’t start at power-on | n
F1 | Fans operating mode with SET >= do: (cn, on, cY, oY) cn= in runs with the compressor, OFF during defrost; on= continuous mode, OFF uring defrost;; cY= runs with the compressor, ON during defrost; oY= continuous mode, ON during defrost. | oy | oy | when you are on site, Please change F1 to oy and F2 to on
F2 | Fans operating mode with SET < do: (cn, on, cY, oY) cn= in runs with the compressor, OFF during defrost; on= continuous mode, OFF during defrost;; cY= runs with the compressor, ON during defrost; oY= continuous mode, ON during defrost. | on | on
Fd | Fans delay after defrost: (0÷99 min) Interval between end of defrost and evaporator fans start. | 2
FS | Fans stop temperature: (-55÷50°C / -67°F ÷ 99°F) setting of temperature, detected by evaporator probe, above which fans are always OFF. | 99℉
Fn | Fan ON time: (0÷15 min) with F1 or F2 = Cn or Cy, (fan activated in parallel with compressor). it sets the evaporator fan ON cycling time when the compressor is off. With Fn =0 and FF ≠ 0 the fan are always off, with Fn=0 and FF =0 the fan are always off. | 1
FF | Fan OFF time: (0÷15 min) with F1 or F2 = Cn or Cy, (fan activated in parallel with compressor). it sets the evaporator fan off cycling time when the compressor is off. With Fn =0 and FF ≠ 0 the fan are always off, with Fn=0 and FF =0 the fan are always off. | 3
AL | Minimum temperature alarm: (-55÷AU°C /-67÷AU°F) when this temperature is reached the alarm is enabled, after the “Ad” delay time. | -67℉
AU | Maximum temperature alarm: (AL÷99°C/99°F) when this emperature is reached the alarm is enabled, after the “Ad” delay time. | 99℉
Ad | Temperature alarm delay: (0÷99 min) time interval between the detection of an alarm condition and alarm signalling. | 60
dA | Exclusion of temperature alarm at startup: (0÷99 min) time interval between the detection of the temperature alarm condition after instrument power on and alarm signalling. | 90
iP | Digital input polarity: (oP ÷ cL) oP= activated by closing the contact; cL= activated by opening the contact; | cL
iF | Digital input configuration: (EA/bA/do/dF/Au/Hc) EL= external alarm: “EA” message is displayed; bA= serious alarm “CA” message is displayed; PA = do not set it; do= door switch function; dF= defrost activation; Au =not used; Hc= inversion of the kind of action; Fn, ES = do not set it | EL
di | Digital input delay: (0÷99 min) with iF=EA or bA delay between the detection of the external alarm condition and its signalling. . With iF=do it represents the delay to activate the door open alarm. | 5
dC | Compressor and fan status when open door: (no/Fn/cP/Fc): no= normal; Fn = Fans OFF; cP =Compressor OFF; Fc = Compressor and fans OFF; | Fn
rd | Regulation with door open: (n÷y) n = no regulation if door is pened; Y= when di is elapsed regulation restarts even if door open alarm is present; | y

## C Freezer
Code | Decription | From Factory
Hy | Differential: (0,1°C  25°C / 1°F ÷ 45°F) Intervention differential for set point. Compressor Cut IN is SET POINT + differential (Hy). Compressor Cut OUT is when the temperature reaches the set point. | 4℃
LS | Minimum SET POINT: (-55°C÷SET/-67°F÷SET): Sets the minimum value for the set point.. | -20℃
US | Maximum SET POINT: (SET÷99°C/ SET÷99°F). Set the maximum value for set point. | -10℃
ot | First probe calibration: (-9.9÷9.9°C / -17°F ÷ 17°F) allows to adjust possible offset of the first probe. | 0
P2 | Evaporator probe presence: n= not present; y= the defrost stops by temperature. | y
oE | Second probe calibration: (-9.9÷9.9°C / -17°F ÷ 17°F) allows to adjust possible offset of the second probe. | 0
od | Outputs activation delay at start up: (0÷99min) This function is enabled at the initial start-up of the instrument and inhibits any output activation for the period of time set in the parameter. | 3
AC | Anti-short cycle delay: (0÷50 min) minimum interval between the compressor stop and the following restart. | 5
Cy | Compressor ON time with faulty probe: (0÷99 min) time during which the compressor is active in case of faulty thermostat probe. With Cy=0 compressor is always OFF. | 15
Cn | Compressor OFF time with faulty probe: (0÷99 min) time during which the compressor is OFF in case of faulty thermostat probe. With Cn=0 compressor is always active. | 15
CF | Measurement unit: (°C÷°F) °C =Celsius; °F =Fahrenheit. WARNING: When the measurement unit is changed the SET point and the values of the parameters Hy, LS, US, oE, o1, AU, AL have to be checked and modified if necessary. | ℃
rE | Resolution (only for °C):(dE ÷ in) dE= decimal between -9.9 and 9.9°C; in= integer | in
Ld |  | P1
dy | Display delay: (015 min.) when the temperature increases, the display is updated of 1 °C/1°F after this time. | 1
td | Defrost type: (EL, in, Ar) EL= electrical heater, compressor OFF; in= hot gas, compressor ON; Ar: defrost according to the value of SET and “do” parameters following conditions: SET > = do: compr. relay off, defrost relay off, fan according to F1 SET < do: compr. relay off, defrost relay on, fan according to F2 | Ar-None GR in-GR unit
dE | Defrost termination temperature: (-55÷50°C / -67÷99°F) if P2=Y it sets the temperature measured by the evaporator probe, which causes the end of defrost. | 13℃
do | Set for fan regulation: (-55÷50°C / -67÷99°F); See parameters F1 and F2 | -2
id | Interval between defrost cycles: (0÷99 minutes) Determines the time interval between the beginning of two defrost cycles. | 6
Nd | Maximum length for defrost: (0÷99 min. with 0 no defrost) when P2=n, (not evaporator probe: timed defrost) it sets the defrost duration, when P2 = y (defrost end based on temperature) it sets the maximum length for defrost. | 30
dd | Start defrost delay: ( 0÷99min) This is useful when different defrost start times are necessary to avoid overloading the plant | 1
dF | Display during defrost: (rt / it / SP / dF) rt= real temperature; it= start defrost temperature; SP=SET-POINT; dF= label dF. | it
dt | Drip time: (0÷99 min) time interval between reaching defrost rmination temperature and the restoring of the control’s normal operation. This time allows the evaporator to eliminate water drops that might have formed due to defrost. | 2
dP | Defrost at power –on: (y÷n) y= at power on defrost starts; n= defrost doesn’t start at power-on | n
F1 | Fans operating mode with SET >= do: (cn, on, cY, oY) cn= in runs with the compressor, OFF during defrost; on= continuous mode, OFF uring defrost;; cY= runs with the compressor, ON during defrost; oY= continuous mode, ON during defrost. | oy
F2 | Fans operating mode with SET < do: (cn, on, cY, oY) cn= in runs with the compressor, OFF during defrost; on= continuous mode, OFF during defrost;; cY= runs with the compressor, ON during defrost; oY= continuous mode, ON during defrost. | on
Fd | Fans delay after defrost: (0÷99 min) Interval between end of defrost and evaporator fans start. | 2
FS | Fans stop temperature: (-55÷50°C / -67°F ÷ 99°F) setting of temperature, detected by evaporator probe, above which fans are always OFF. | 50℃
Fn | Fan ON time: (0÷15 min) with F1 or F2 = Cn or Cy, (fan activated in parallel with compressor). it sets the evaporator fan ON cycling time when the compressor is off. With Fn =0 and FF ≠ 0 the fan are always off, with Fn=0 and FF =0 the fan are always off. | 1
FF | Fan OFF time: (0÷15 min) with F1 or F2 = Cn or Cy, (fan activated in parallel with compressor). it sets the evaporator fan off cycling time when the compressor is off. With Fn =0 and FF ≠ 0 the fan are always off, with Fn=0 and FF =0 the fan are always off. | 3
AL | Minimum temperature alarm: (-55÷AU°C /-67÷AU°F) when this temperature is reached the alarm is enabled, after the “Ad” delay time. | -55℃
AU | Maximum temperature alarm: (AL÷99°C/99°F) when this emperature is reached the alarm is enabled, after the “Ad” delay time. | 99℃
Ad | Temperature alarm delay: (0÷99 min) time interval between the detection of an alarm condition and alarm signalling. | 60
dA | Exclusion of temperature alarm at startup: (0÷99 min) time interval between the detection of the temperature alarm condition after instrument power on and alarm signalling. | 90
iP | Digital input polarity: (oP ÷ cL) oP= activated by closing the contact; cL= activated by opening the contact; | cL
iF | Digital input configuration: (EA/bA/do/dF/Au/Hc) EL= external alarm: “EA” message is displayed; bA= serious alarm “CA” message is displayed; PA = do not set it; do= door switch function; dF= defrost activation; Au =not used; Hc= inversion of the kind of action; Fn, ES = do not set it | EL
di | Digital input delay: (0÷99 min) with iF=EA or bA delay between the detection of the external alarm condition and its signalling. . With iF=do it represents the delay to activate the door open alarm. | 5
dC | Compressor and fan status when open door: (no/Fn/cP/Fc): no= normal; Fn = Fans OFF; cP =Compressor OFF; Fc = Compressor and fans OFF; | Fn
rd | Regulation with door open: (n÷y) n = no regulation if door is pened; Y= when di is elapsed regulation restarts even if door open alarm is present; | y

## Condenser fan
Code | Decription | From Factory
Hy | Differential: (0,1°C  25°C / 1°F ÷ 45°F) Intervention differential for set point. Compressor Cut IN is SET POINT + differential (Hy). Compressor Cut OUT is when the temperature reaches the set point. | 5°C
LS | Minimum SET POINT: (-55°C÷SET/-67°F÷SET): Sets the minimum value for the set point.. | 0°C
US | Maximum SET POINT: (SET÷99°C/ SET÷99°F). Set the maximum value for set point. | 65°C
ot | First probe calibration: (-9.9÷9.9°C / -17°F ÷ 17°F) allows to adjust possible offset of the first probe. | 0
P2 | Evaporator probe presence: n= not present; y= the defrost stops by temperature. | n
oE | Second probe calibration: (-9.9÷9.9°C / -17°F ÷ 17°F) allows to adjust possible offset of the second probe. | 0
od | Outputs activation delay at start up: (0÷99min) This function is enabled at the initial start-up of the instrument and inhibits any output activation for the period of time set in the parameter. | 0
AC | Anti-short cycle delay: (0÷50 min) minimum interval between the compressor stop and the following restart. | 1
Cy | Compressor ON time with faulty probe: (0÷99 min) time during which the compressor is active in case of faulty thermostat probe. With Cy=0 compressor is always OFF. | 1
Cn | Compressor OFF time with faulty probe: (0÷99 min) time during which the compressor is OFF in case of faulty thermostat probe. With Cn=0 compressor is always active. | 5
CF | Measurement unit: (°C÷°F) °C =Celsius; °F =Fahrenheit. WARNING: When the measurement unit is changed the SET point and the values of the parameters Hy, LS, US, oE, o1, AU, AL have to be checked and modified if necessary. | °C
rE | Resolution (only for °C):(dE ÷ in) dE= decimal between -9.9 and 9.9°C; in= integer | in
Ld |  | P1
dy | Display delay: (015 min.) when the temperature increases, the display is updated of 1 °C/1°F after this time. | 0
dE | Defrost termination temperature: (-55÷50°C / -67÷99°F) if P2=Y it sets the temperature measured by the evaporator probe, which causes the end of defrost. | 8°C
do | Set for fan regulation: (-55÷50°C / -67÷99°F); See parameters F1 and F2 | 0°C
id | Interval between defrost cycles: (0÷99 minutes) Determines the time interval between the beginning of two defrost cycles. | 0
Nd | Maximum length for defrost: (0÷99 min. with 0 no defrost) when P2=n, (not evaporator probe: timed defrost) it sets the defrost duration, when P2 = y (defrost end based on temperature) it sets the maximum length for defrost. | 0
dd | Start defrost delay: ( 0÷99min) This is useful when different defrost start times are necessary to avoid overloading the plant | 0
dF | Display during defrost: (rt / it / SP / dF) rt= real temperature; it= start defrost temperature; SP=SET-POINT; dF= label dF. | it
F1 | Fans operating mode with SET >= do: (cn, on, cY, oY) cn= in runs with the compressor, OFF during defrost; on= continuous mode, OFF uring defrost;; cY= runs with the compressor, ON during defrost; oY= continuous mode, ON during defrost. | oy
F2 | Fans operating mode with SET < do: (cn, on, cY, oY) cn= in runs with the compressor, OFF during defrost; on= continuous mode, OFF during defrost;; cY= runs with the compressor, ON during defrost; oY= continuous mode, ON during defrost. | on
Fd | Fans delay after defrost: (0÷99 min) Interval between end of defrost and evaporator fans start. | 0
FS | Fans stop temperature: (-55÷50°C / -67°F ÷ 99°F) setting of temperature, detected by evaporator probe, above which fans are always OFF. | 99
Fn | Fan ON time: (0÷15 min) with F1 or F2 = Cn or Cy, (fan activated in parallel with compressor). it sets the evaporator fan ON cycling time when the compressor is off. With Fn =0 and FF ≠ 0 the fan are always off, with Fn=0 and FF =0 the fan are always off. | 1
FF | Fan OFF time: (0÷15 min) with F1 or F2 = Cn or Cy, (fan activated in parallel with compressor). it sets the evaporator fan off cycling time when the compressor is off. With Fn =0 and FF ≠ 0 the fan are always off, with Fn=0 and FF =0 the fan are always off. | 3
AL | Minimum temperature alarm: (-55÷AU°C /-67÷AU°F) when this temperature is reached the alarm is enabled, after the “Ad” delay time. | 10
AU | Maximum temperature alarm: (AL÷99°C/99°F) when this emperature is reached the alarm is enabled, after the “Ad” delay time. | 90
Ad | Temperature alarm delay: (0÷99 min) time interval between the detection of an alarm condition and alarm signalling. | 0
dA | Exclusion of temperature alarm at startup: (0÷99 min) time interval between the detection of the temperature alarm condition after instrument power on and alarm signalling. | 0
iP | Digital input polarity: (oP ÷ cL) oP= activated by closing the contact; cL= activated by opening the contact; | cL
iF | Digital input configuration: (EA/bA/do/dF/Au/Hc) EL= external alarm: “EA” message is displayed; bA= serious alarm “CA” message is displayed; PA = do not set it; do= door switch function; dF= defrost activation; Au =not used; Hc= inversion of the kind of action; Fn, ES = do not set it | Au
di | Digital input delay: (0÷99 min) with iF=EA or bA delay between the detection of the external alarm condition and its signalling. . With iF=do it represents the delay to activate the door open alarm. | 0
dC | Compressor and fan status when open door: (no/Fn/cP/Fc): no= normal; Fn = Fans OFF; cP =Compressor OFF; Fc = Compressor and fans OFF; | no
rd | Regulation with door open: (n÷y) n = no regulation if door is pened; Y= when di is elapsed regulation restarts even if door open alarm is present; | n
Setting temp | Setting temp | 55°C

## Sheet2
HOW TO ENTER THE HIDDEN MENU 1. Enter the Programming mode by pressing the SET+DOWN keys for 3s (“°F” LED starts blinking). 2. Released the keys, then push again the SET+DOWN keys for more than 7s. The L2 label will be displayed immediately followed from the Hy parameter. NOW YOU ARE IN THE HIDDEN MENU. 3. Use Arrow " UP " to find Parameter " US " 4. Press the “SET” key to display its value 5. Use UP change its value to 20. 6. Press “SET” to store the new value 7.To exit: Press SET+UP or wait 15s without pressing a key. 8.Setting temp: Hold "SET" for 3s, then change its value to 13F, press Set to save.
Note: There is 6 degrees differential for compressor cutting in & out. If you need temp around 14 F, you may set temp at 12 F.